## AV EQUIPMENT ROOM CHECKLIST
PRIORITY |  |  | LEGACY MINIMUM | UHS IT STANDARD
| GENERAL | DATE / TIME |  |  | DATE AND TIME
|  | INSPECTOR NAME |  |  | #
|  | CAMPUS |  |  | CLEAR LAKE | DOWNTOWN | MAIN | VICTORIA
|  | BUILDING |  |  | TEXT
|  | ROOM NUMBER |  |  | TEXT
HIGH |  | TEMPERATURE | 60 - 75F | 60 - 75F | #
HIGH |  | HUMIDITY | 30 - 50% RH | 30 - 50% RH | #
HIGH |  | ASSET TAG ON DOOR FRAME | YES | YES | YES | NO | DAMAGED
MED |  | CONTROLLABLE THERMOSTAT | YES | YES | YES | NOT CONTROLLABLE | NONE IN ROOM
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | ROOM INFORMATION | ROOM TYPE | SHARED MOSTLY IT | DEDICATED | DEDICATED | SHARED MOSTLY IT | SHARED MOSTLY OTHERS
HIGH |  | ACCESS | READER OR IT MASTER KEY | READER W/ IT MASTER KEY | READER W/ IT MASTER KEY | MASTER KEY | COMMON KEYED | NONE
HIGH |  | CAMERA INTERIOR | YES | YES | YES | NO |  | NON OPERATIONAL
US |  | CAMERA EXTERIOR | YES OR NOT REQUIRED | YES OR NOT REQUIRED | YES | NO | NOT REQUIRED | NON OPERATIONAL
HIGH |  | DOOR TYPE | SOLID | SOLID | SOLID | LOUVERED | GLASS
MED |  | ROOM LABEL | YES | YES | YES | NO
MED |  | DOOR SWING | DOES NOT AFFECT ROOM USE | OUT | OUT | IN | AFFECTS ROOM USE
HIGH |  | LIGHTING | OPERATIONAL | SWITCH | SWITCH | MOTION | NONE | SWITCH NON OPERATIONAL | MOTION NON OPERATIONAL
HIGH |  | WALLS TO DECK | YES | YES | YES | NO
LOW |  | CEILING | ANY | OPEN/NONE | OPEN/NONE | SHEETROCK | CEILING TILE
|  | FIRE SUPPRESSION | ANY | PRE-ACTION | BUILDING STANDARD | PRE-ACTION | CLEAN AGENT | NONE (EXTIGUISHER REQ)
LOW |  | SPRINKLER HEADS | CAGED | CAGED | CAGED | NOT CAGED | NONE
HIGH |  | INSPECTED FIRE EXTINGUISHER | IF NO FIRE SUPPRESSION | NOT REQUIRED | NOT REQUIRED | CO2 OR CLEAN AGENT | WET TYPE (REPLACE) | INSPECTION REQUIRED
HIGH |  | POWER CORD TRIPPING HAZARD | NO | NO | NO | YES
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | HOUSE KEEPING | TRASH IN ROOM | NO | NO | NO | YES, REMOVE
LOW |  | FLOOR IS CLEAN | YES | YES | YES | NO, CLEANING REQUIRED
LOW |  | EQUIPMENT DUST FREE | YES | YES | YES | NO, CHECK ROOM PRESSURE
MED |  | INAPROPRIATE STORAGE | NO | NO | NO | YES
HIGH |  | ABANDONED CABLING | NO | NO | NO | YES
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | NON SERVICING SYSTEMS | WATER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | SEWER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | FIRE MAIN | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ROOF DRAINS | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ELECTRICAL PANELS | NO OR SERVICES ROOM | NO | NO | YES, SERVICES ROOM | YES, NOT ACCEPTABLE
HIGH US |  | ACCESS CONTROL PANELS | NO | NO | NO | YES, ACCEPTABLE | YES, NOT ACCEPTABLE
HIGH US |  | IT SYSTEMS | NO OR YES, ACCEPTABLE | NO OR YES, ACCEPTABLE | NO | YES, ACCEPTABLE | YES, NOT ACCEPTABLE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
MED | ROOM CABLE SUPPORT | OVERHEAD CABLE SUPPORT | ANY (NOT NONE) | ANY (NOT NONE) | BASKET | LADDER | HOOKS | NONE, SUPPORT REQUIRED
MED |  | WALL CABLE SUPPORT | ANY (NOT NONE) | ANY (NOT NONE) | BASKET | LADDER | D-RINGS | NONE, SUPPORT REQUIRED
MED |  | SUPPORT CAPACITY | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | TRAY FULL | REWORK REQUIRED
LOW |  | CABLE TRAY DRESSING | NEAT AND TIDY | NEAT AND TIDY | NEAT AND TIDY | REDRESSING REQUIRED
HIGH |  | HORIZONTAL PENETRATIONS | COMPLIANT OR SEALED | COMPLIANT OR SEALED | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | HORZ. PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | VERTICAL PENETRATIONS | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | NOT APPLICABLE
MED |  | VERTL PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | MEP | LIGHTS | EMERGENCY | EMERGENCY | EMERGENCY | HOUSE POWER | NOT SUFFICIENT | UNKNOWN SUFFICIENT
HIGH |  | HVAC | DEDICATED | DEDICATED | DEDICATED | BUILDING AIR | NONE | UNKNOWN
|  | HVAC TYPE | ANY | ANY | CHILLED WATER | DX | BOTH | UNKNOWN
MED |  | WALL POWER | EMERGENCY OR HOUSE | EMERGENCY OR HOUSE | EMERGENCY | HOUSE POWER | NONE | UNKNOWN
HIGH |  | RACK POWER -TWIST LOCK | EMERGENCY OR HOUSE | EMERGENCY OR HOUSE | EMERGENCY | HOUSE POWER | NONE
HIGH |  | RACK POWER - NON LOCKING | EMERGENCY OR HOUSE | EMERGENCY OR HOUSE | EMERGENCY | HOUSE POWER | NONE
MED |  | POSITIVE PRESSURE | YES | YES | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| RACK RELATED | NUMBER OF RACKS/CABINETS |  |  | 1 | 2 | 3
MED |  | RACK 1 SPARE RACK UNITS | 5 RU OR MORE |  | #
MED |  | RACK 2 SPARE RACK UNITS |  |  | #
MED |  | RACK 3 SPARE RACK UNITS |  |  | #
MED |  | SPARE PATCH PANEL PORTS |  |  | # | #
LOW |  | LACING BARS | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | REDRESSING REQUIRED | FULL | NONE
HIGH |  | FRONT CLEARANCE | NOT UNSAFE | 3FT+ | 3FT+ | 2FT+ | NONE | UNSAFE
HIGH |  | REAR CLEARANCE | NOT UNSAFE | 3FT+ | 3FT+ | 2FT+ | NONE | UNSAFE
LOW |  | ROOM FOR ADDITIONAL RACK | YES OR EMPTY RACKS AVAIL. | YES OR EMPTY RACKS AVAIL. | YES | NO, EMPTY RACKS AVAILABLE | NONE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
US | UPS | UPS SIZE | ANY | NA | 1500W | 5000W | 3000W | NONE
HIGH |  | UPS STATUS | PASSED TEST | PASSED TEST | PASSED TEST | FAILS TEST | NONE
MED |  | UPS MONITORED | YES | YES | YES | NO
MED |  | ROOM TEMP MONITORING | YES | YES | YES | NO
|  | STEP DOWN TRANSFORMER | CAMPUS SPECIFIC | CAMPUS SPECIFIC | YES | NO | NA
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | LABELING | ROOM | YES | YES | YES | NO
LOW |  | RACKS | YES | YES | YES | NO
LOW |  | DATA CABLES | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | VIDEO CABLES | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | AUDIO CABLES | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | POWER CABLES | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | AV EQUIPMENT | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | HORIZONTAL PATCH PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | SWITCHES | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | UPS | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BUSS BAR | YES | YES | YES | N/A | UPDATE REQUIRED
HIGH |  | FIRE STOP ASSEMBLIES | YES | YES | YES | NO | UPDATE REQUIRED

## AV WORK ROOM CHECKLIST
PRIORITY |  |  | LEGACY MINIMUM | UHS IT STANDARD
| GENERAL | DATE / TIME |  |  | DATE AND TIME
|  | INSPECTOR NAME |  |  | #
|  | CAMPUS |  |  | CLEAR LAKE | DOWNTOWN | MAIN | VICTORIA
|  | BUILDING |  |  | TEXT
|  | ROOM NUMBER |  |  | TEXT
MED |  | TEMPERATURE | 60 - 75F | 60 - 75F | #
MED |  | HUMIDITY | 30 - 50% RH | 30 - 50% RH | #
HIGH |  | ASSET TAG ON DOOR FRAME | YES | YES | YES | DAMAGED | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | ROOM INFORMATION | ROOM TYPE | SHARED MOSTLY IT | DEDICATED | DEDICATED | SHARED MOSTLY IT | SHARED MOSTLY OTHERS
HIGH |  | ACCESS | READER OR IT MASTER KEY | READER W/ IT MASTER KEY | READER W/ IT MASTER KEY | IT MASTER KEYED | COMMON KEYED | NONE
HIGH |  | CAMERA INTERIOR | YES | YES | YES | NO |  | NON OPERATIONAL
US |  | CAMERA EXTERIOR | YES OR NOT REQUIRED | YES OR NOT REQUIRED | YES | NO | NOT REQUIRED | NON OPERATIONAL
HIGH |  | DOOR TYPE | SOLID | SOLID | SOLID | LOUVERED | GLASS
MED |  | ROOM LABEL | YES | YES | YES | NO
MED |  | DOOR SWING | DOES NOT AFFECT ROOM USE | OUT | OUT | IN | AFFECTS ROOM USE
HIGH |  | LIGHTING | OPERATIONAL | SWITCH | SWITCH | MOTION | NONE | SWITCH NON OPERATIONAL | MOTION NON OPERATIONAL
HIGH |  | WALLS TO DECK | YES | YES | YES | NO
LOW |  | CEILING | ANY | OPEN/NONE | OPEN/NONE | SHEETROCK | CEILING TILE
|  | FIRE SUPPRESSION | ANY | ANY | BUILDING STANDARD | PRE-ACTION | CLEAN AGENT | NONE (EXTIGUISHER REQ)
MED |  | WORKSTATION | YES | YES | YES | NO, SPACE AVAILABLE | SPACE NOT AVAILABLE
LOW |  | WORK BENCH | ANY | YES | YES | NO, SPACE AVAILABLE | SPACE NOT AVAILABLE
MED |  | SPACE FOR GROWTH | YES | YES | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | HOUSE KEEPING | TRASH IN ROOM | NO | NO | NO | YES, REMOVE
LOW |  | FLOOR IS CLEAN | YES | YES | YES | NO, CLEANING REQUIRED
LOW |  | EQUIPMENT DUST FREE | YES | YES | YES | NO, CHECK ROOM PRESSURE
MED |  | INAPROPRIATE STORAGE | ANY | ANY | NO | YES
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | NON SERVICING SYSTEMS | WATER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | SEWER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | FIRE MAIN | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ROOF DRAINS | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ELECTRICAL PANELS | NO OR SERVICES ROOM | NO | NO | YES, SERVICES ROOM | YES, NOT ACCEPTABLE
HIGH US |  | ACCESS CONTROL PANELS | NO | NO | NO | YES, ACCEPTABLE | YES, NOT ACCEPTABLE
HIGH US |  | IT SYSTEMS | NO OR YES, ACCEPTABLE | NO OR YES, ACCEPTABLE | NO | YES, ACCEPTABLE | YES, NOT ACCEPTABLE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
MED | ROOM CABLE SUPPORT | OVERHEAD CABLE SUPPORT | ANY (NOT NONE) | ANY (NOT NONE) | BASKET | LADDER | HOOKS | NONE, SUPPORT REQUIRED
MED |  | WALL CABLE SUPPORT | ANY (NOT NONE) | ANY (NOT NONE) | BASKET | LADDER | D-RINGS | NONE, SUPPORT REQUIRED
MED |  | SUPPORT CAPACITY | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | TRAY FULL | REWORK REQUIRED
LOW |  | CABLE TRAY DRESSING | NEAT AND TIDY | NEAT AND TIDY | NEAT AND TIDY | REDRESSING REQUIRED
HIGH |  | HORIZONTAL PENETRATIONS | COMPLIANT OR SEALED | COMPLIANT OR SEALED | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | HORZ. PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | VERTICAL PENETRATIONS | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | NOT APPLICABLE
MED |  | VERTL PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | MEP | LIGHTS | EMERGENCY OR HOUSE | EMERGENCY OR HOUSE | EMERGENCY | HOUSE POWER | NOT SUFFICIENT | UNKNOWN SUFFICIENT
HIGH |  | HVAC | DEDICATED OR BUILDING | DEDICATED OR BUILDING | DEDICATED | BUILDING AIR | NONE | UNKNOWN
|  | HVAC TYPE | CAMPUS SPECIFIC | CAMPUS SPECIFIC | CHILLED WATER | DX | BOTH | UNKNOWN
MED |  | WALL POWER | EMERGENCY OR HOUSE | EMERGENCY OR HOUSE | EMERGENCY | HOUSE POWER | NONE | UNKNOWN
HIGH |  | WORKSTATION POWER | EMERGENCY OR HOUSE | EMERGENCY OR HOUSE | EMERGENCY | HOUSE POWER | NONE
HIGH |  | WORK BENCH POWER | EMERGENCY OR HOUSE | EMERGENCY OR HOUSE | EMERGENCY | HOUSE POWER | NONE
MED |  | POSITIVE PRESSURE | YES | YES | YES | NO

## AV STORAGE ROOM CHECKLIST
PRIORITY |  |  | LEGACY MINIMUM | UHS IT STANDARD
| GENERAL | DATE / TIME |  |  | DATE AND TIME
|  | INSPECTOR NAME |  |  | #
|  | CAMPUS |  |  | CLEAR LAKE | DOWNTOWN | MAIN | VICTORIA
|  | BUILDING |  |  | TEXT
|  | ROOM NUMBER |  |  | TEXT
MED |  | TEMPERATURE | 60 - 75F | 60 - 75F | #
MED |  | HUMIDITY | 30 - 50% RH | 30 - 50% RH | #
HIGH |  | ASSET TAG ON DOOR FRAME | YES | YES | YES | DAMAGED, REPLACE | NONE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | ROOM INFORMATION | ROOM TYPE | SHARED MOSTLY IT | DEDICATED | DEDICATED | SHARED MOSTLY IT | SHARED MOSTLY OTHERS
HIGH |  | ACCESS | READER OR IT MASTER KEY | READER W/ IT MASTER KEY | CARD WITH IT MASTER KEY | IT MASTER KEYED | COMMON KEYED | NONE
HIGH |  | CAMERA INTERIOR | YES | YES | YES | NO |  | NON OPERATIONAL
HIGH |  | CAMERA EXTERIOR | YES OR NOT REQUIRED | YES OR NOT REQUIRED | YES | NO | NOT REQUIRED | NON OPERATIONAL
HIGH |  | DOOR TYPE | SOLID | SOLID | SOLID SINGLE | SOLID DOUBLE | LOUVERED DOUBLE | SOLID DOUBLE
MED |  | ROOM LABEL | YES | YES | YES | NO
MED |  | DOOR SWING | DOES NOT AFFECT ROOM USE | OUT | OUT | IN | AFFECTS ROOM USE
HIGH |  | LIGHTING | OPERATIONAL | SWITCH | SWITCH | MOTION | NONE | SWITCH NON OPERATIONAL | MOTION NON OPERATIONAL
HIGH |  | WALLS TO DECK | YES | YES | YES | NO
LOW |  | CEILING | ANY | OPEN/NONE | OPEN/NONE | SHEETROCK | CEILING TILE
|  | FIRE SUPPRESSION | ANY | ANY | BUILDING STANDARD | PRE-ACTION | CLEAN AGENT | NONE (EXTIGUISHER REQ)
MED |  | SPRINKLER HEADS | ANY | ANY | STANDARD | CAGED | EXTINGUISHER | NONE (EXTIGUISHER REQ)
LOW |  | FIRE EXTINGUISHER | IF NO FIRE SUPPRESSION | NOT REQUIRED | NOT REQUIRED | YES, INSPECTION CURRENT | YES, INSPECTION EXPIRED | NONE (EXTIGUISHER REQ)
MED |  | SPACE FOR GROWTH | YES | YES | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | HOUSE KEEPING | TRASH IN ROOM | NO | NO | NO | YES, REMOVE
LOW |  | FLOOR IS CLEAN | YES | YES | YES | NO, CLEANING REQUIRED
LOW |  | EQUIPMENT DUST FREE | YES | YES | YES | NO, CLEANING REQUIRED
LOW |  | STORAGE RACKS OR SHELVES | ANY | ANY | YES | NO
MED |  | FURNITURE STORAGE | NO | NO | NO | YES
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | NON SERVICING SYSTEMS | WATER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | SEWER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | FIRE MAIN | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ROOF DRAINS | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
MED |  | ELECTRICAL PANELS | NO | NO | NO | YES, SERVICES ROOM | YES, NOT ACCEPTABLE
MED |  | ACCESS CONTROL PANELS | NO | NO | NO | YES, ACCEPTABLE | YES, NOT ACCEPTABLE
MED |  | AV SYSTEMS | NO | NO | NO | YES, ACCEPTABLE | YES, NOT ACCEPTABLE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | MEP | LIGHTS | EMERGENCY OR HOUSE | EMERGENCY OR HOUST | EMERGENCY | HOUSE POWER | NOT SUFFICIENT | UNKNOWN SUFFICIENT
MED |  | HVAC | BUILDING OR DEDICATED | BUILDING OR DEDICATED | BUILDING AIR | DEDICATED | NONE | UNKNOWN
MED |  | WALL POWER | EMERGENCY OR HOUSE | EMERGENCY OR HOUSE | EMERGENCY | HOUSE POWER | NONE | UNKNOWN
MED |  | CHARGING STATION POWER | EMERGENCY OR HOUSE | EMERGENCY OR HOUSE | EMERGENCY | HOUSE POWER | NONE | N/A